“Application Objects” Stencil Operation

R. Koch,  1-16-06


Background

The IA Series BACnet controllers do not currently support the DUI object.  Until support is added, an application performing the same basic function was created and tested.  This application was created as a custom object named “DUI_App”.  It was tested for use with the DUIC-5P-12V interface module and all IA Series BACnet controllers.  This custom object must be used with an “Analog Input” object whose “Type” property is set to “6 – Resistance 1K” and is connected to a physical UI point.  

Distribution Form

Since the application is a custom object, we are able to distribute it in a more efficient manner, where it is part of a custom stencil.  This custom stencil is named “Application Objects”.  By doing it in this manner, it will have a similar look and feel to it as the other standard controller objects do.  Additionally, this approach can be the starting point of offering other custom objects performing specific functions requested by our field offices.

Installation

With Visio\WP-Tech closed, place the custom “Application Objects” stencil in the “C:\Program Files\WorkPlaceTech\Solutions” directory so that all users on that PC can have access to it.  Once the custom stencil is in this location, it can be opened from within WP-Tech by selecting “File – Shapes – Application Objects” from the menu on Visio 2003 or “File – Stencils – C:\…Solutions – Application Objects” from the menu on Visio 2002.  The stencil will be docked along with the default controller stencils on the left side of the page.  Once opened, it can be treated like any other stencil used by WP-Tech.  The DUI_App object can be dragged from the stencil onto a drawing as many times as is required.  Since the object is based on a custom object, its use must abide by all the same rules and requirements.  Therefore, each time the object is placed on a drawing, WP-Tech will create another drawing page containing its the application logic.  Typically, no user calibration should be required since the application follows the same resistance table used for the IA Series LonMark controllers.

Messages Displayed When Using Custom Stencils  

Depending upon which version of Visio is being used (Visio 2002 or Visio 2003), the user may see warning messages when opening or closing the custom stencil and/or a drawing that was saved with the stencil open.  These messages and their responses are documented below in an effort to eliminate the confusion they may cause.

WP-Tech using Visio 2002

When the stencil is opened from within a drawing, the system will display the following warning window.  Simple respond to it by clicking “OK”.  This warning message will be displayed anytime the stencil is opened or a drawing containing this stencil is opened.

[image: image1.jpg]Mactos in this document are cisabled because the securiy level i high, and the macros have not been digtally sioned or verfied as safe. Tarun the.
macros, you can ether have them signed or change your security level





No other messages should be displayed as a result of using the custom stencil.

WP-Tech using Visio 2003

When the stencil is used within the Visio 2003 environment, 3 different windows will be displayed.  Two will appear any time the stencil is opened or a drawing with the stencil saved within it is opened.  One will appear any time the stencil is closed or a drawing containing the stencil is closed.

When the stencil is opened from within a drawing, the system will first display the following warning window.  Simply respond to it by clicking “Enable Macros”. 

[image: image2.jpg]Security Warning

*C:iprogram FlestInvensys|WarkPlaceTechiSolutions|Applcation Objects.vss'
cantains macros,

Macros may contain viruses, It i usually safe to disable macros, but f the
macros are legtimate, you might lase some functianalty.

e | T | T





Then, the following warning window will be displayed.  Respond to it by clicking “Yes”.

[image: image3.jpg]Microsoft Office Visio

This appication is abouk to ntiaize ActiveX controls that might be unsafe. I you trust the source of this document,
select Yes and the cantrol il e intialzed Using your dacument settings.





After the second window disappears, the stencil will be opened and docked to the left side of the drawing.  At this point, it can be used like any other stencil.  The DUI_App object can be placed on the drawing as many times as is required.

The last message will be displayed anytime the stencil is closed or a drawing containing the stencil is closed.

[image: image4.jpg][ Hicrosoft 0

isio I8
LA\ sove chocesto apicatn bt 57





Always respond to it by clicking “No”.  To make the custom stencil compatible with both Visio 2002 and Visio 2003, it was created using WP-Tech with Visio 2002.  This message detects that fact and prompts the user to save it since the system converted it for use in Visio 2003.  By not saving the stencil in Visio 2003 format, it can remain compatible with both versions of Visio.  

If the dual version compatibility of the custom stencil is not required, you can respond to the prompt by clicking “Yes” and assigning the stencil a new name.  If “Yes” is selected, the following window will be displayed.  Click “OK”

[image: image5.jpg]Microsoft O

L\, T eisreatonty Tosave copy, ek, th e thedocuent e e e v s S box

=





Then the following window is displayed.  Enter a new name such as “Application Objects 2003” and click “Save”.  This saves the updated copy into the correct directory using the new name.

[image: image6.jpg]save

| & solutons v® 2 QXc

©

My Recent
Documents

@
[

My Documents

)
e

My Network.
Places.

Cacnet
Smiso

S0

o0

s

Sz

Smsoo

ey

Sother

(Gapplcaton Objecs 2003.155
(SHapplcation Objects.vs5

T A——

lstencit vss

SHwes arrotation.ves
(WP Custom Objec 01,455
<

e Custom Object ez
WP 10 snd Alarm Contrl 0155
WP 10 snd larm Contrl 02,155
WP 10 snd Alar Contrl 03,155
WP 10 snd Alarm Contrl 04,155
WP 10 and Alarm Contrl 05,155
WP 10 snd Al Contrl 06,155
WP 10 snd Alarm Contrl 07,155
WP 10 snd Alarm Contrl 08,155
WP 10 snd Alar Contrl 09,155
WP 10 snd larm Contrlves
WP Logic and viath Corcl 01455
WP Logic and vth Corcl 0255
WP Logic and vath Corcl 0355
WP Logi and et Control.vs5

Shwes
hwes
hwes
hwes
Shwes

Floome: appication Oects 200955

Save astype: [stencl (*.vss)





Once this has been done, the new copy of the stencil can be used and you will no longer get the prompt to save when closing the stencil.

Page   1  of   3

